Special Instructions for tight tank installation:

1. The tight tank shall be lined, on the inside and outside, with double lining on the tank

bottom, to provide additional protection in case of tank failure.

2. The liner will be a polyvinyl chloride (PVC) flexible membrane liner 50 mil in thickness, and will be field installed with a representative of Miller Environmental Products, Inc.  (Liner manufacturer) present.

3. The tank, with liners, shall be installed onto a level (and compacted) bed of sand,

with a suitable rubber (or equivalent) mat not less than 1/4" in thickness to be placed

between the sand and the external liner.

4. The liner will be field welded (seamed) using proven chemical fusion techniques. As

well as appropriate 6" stainless steel bands and other fasteners (if necessary) to physically hold the liner in place.

5. The liner will be fabricated to provide and effective seal around the inlet pipe and the

manhole riser.

6. A plaque or sign shall be installed, to instruct the septage hauler as to specific

techniques to avoid damaging the liner during routine pumping. The plaque shall read:

"This tank is lined with a PVC Membrane. To avoid puncture, do not use sharp objects within the tank. Miller Environmental Products, Inc. (508) 697-3710"